AFRIPLAN ELECTRICAL

QUOTATION TOOL

COMPREHENSIVE SPECIFICATION DOCUMENT

Parameters, Variables, Standards & Considerations

For the South African Electrical Contracting Market

Version 1.0  |  February 2026

Prepared by: JLWanalytics

# TABLE OF CONTENTS

PART A: GLOBAL PARAMETERS (All Project Types)

- A1. Project Classification Variables

- A2. South African Regulatory Standards

- A3. Pricing Engine Variables

- A4. Labour Cost Model

- A5. Regional Adjustment Factors

- A6. Material Cost Database Structure

PART B: PRIORITY 1 - Commercial + Solar Installations

- B1. Commercial Electrical Parameters

- B2. Solar PV System Parameters

- B3. Battery Storage Parameters

- B4. SSEG Compliance Variables

- B5. Commercial-Specific Standards

PART C: PRIORITY 2 - Residential New Builds

- C1. Dwelling Classification

- C2. Room-by-Room Electrical Requirements

- C3. Circuit Design Parameters

- C4. Dedicated Circuit Specifications

- C5. Residential-Specific Standards

PART D: PRIORITY 3 - Maintenance & COC Renewals

- D1. COC Inspection Parameters

- D2. Defect Classification & Remedial Pricing

- D3. Testing Equipment & Procedures

- D4. COC Document Requirements

PART E: DATA MODEL & FORMULA ENGINE

- E1. Quotation Calculation Formulas

- E2. Database Schema Recommendations

- E3. Price Escalation Model

PART A: GLOBAL PARAMETERS (All Project Types)

These parameters apply universally across all quotation types generated by the AfriPlan Electrical tool. They form the foundation of every calculation.

## A1. Project Classification Variables

Every quotation must first classify the project to determine which parameter set applies.

| Variable | Data Type | Options / Range | Impact on Quote |
| --- | --- | --- | --- |
| project_type | ENUM | residential ¦ commercial ¦ industrial ¦ solar ¦ maintenance_coc | Determines entire parameter set, markup rates, and compliance requirements |
| project_subtype | ENUM | new_build ¦ renovation ¦ extension ¦ tenant_fitout ¦ solar_retrofit ¦ coc_inspection | Affects labour multipliers and material waste factors |
| building_class | ENUM | single_storey ¦ double_storey ¦ multi_storey ¦ complex ¦ warehouse ¦ office | Affects cable run lengths, containment type, and labour difficulty factors |
| construction_phase | ENUM | first_fix ¦ second_fix ¦ complete ¦ remedial | Determines what work is included in scope |
| supply_type | ENUM | single_phase ¦ three_phase | Affects DB board, main breaker, cable sizing, and earthing |
| supply_capacity_amps | INTEGER | 40 ¦ 60 ¦ 80 ¦ 100 ¦ 200 ¦ 400 | Determines main incomer, cable from meter to DB, and protection sizing |
| gross_floor_area_m2 | FLOAT | 20 - 100,000 | Used for cable run estimation, conduit quantity, and lighting calculations |
| number_of_floors | INTEGER | 1 - 50 | Affects vertical cable runs, riser costs, and labour difficulty |
| erf_size_m2 | FLOAT | 150 - 50,000 | Affects outdoor lighting, boundary wall circuits, and earthing |
| municipality | ENUM | tshwane ¦ joburg ¦ ekurhuleni ¦ cape_town ¦ ethekwini ¦ other | Determines meter type, connection fees, and specific bylaws |
| meter_type | ENUM | prepaid ¦ conventional ¦ smart ¦ ct_metered | Affects ready board requirements and metering costs |
| client_type | ENUM | homeowner ¦ developer ¦ body_corporate ¦ business ¦ government | Affects payment terms, markup, and documentation level |

## A2. South African Regulatory Standards

The quotation tool must validate compliance with the following standards. Non-compliance invalidates COC issuance.

| Standard | Full Title | Application | Key Requirements for Tool |
| --- | --- | --- | --- |
| SANS 10142-1:2017 | Wiring of Premises - Low Voltage | ALL electrical installations | Circuit protection, cable sizing, earthing, socket placement heights, DB board specs, earth leakage protection |
| SANS 10142-2:2018 | Wiring of Premises - Medium Voltage | Installations > 1kV (commercial/industrial) | MV switchgear, transformer protection, arc flash calculations |
| SANS 10142-3 | Wiring of Premises - Construction Sites | Temporary installations | Temporary DB, IP ratings, RCD protection on all circuits |
| SANS 10400-XA:2021 | Energy Usage in Buildings | ALL new buildings & major renovations | Energy efficiency, maximum power density (W/m2), hot water systems, lighting efficiency |
| SANS 10400-T | Fire Protection | Commercial & multi-residential | Emergency lighting, fire detection, escape route lighting, fire-rated cables |
| SANS 62305 (NRS 039) | Lightning Protection | Risk assessment required for all buildings | Lightning protection level (LPL), earth electrode system, surge protection |
| SANS 10098-1 | Public Lighting | External and street lighting | Illumination levels, pole specifications, energy efficiency |
| NRS 097-2-3 | Electricity Supply - Grid Interconnection of SSEG | ALL solar/battery installations feeding back to grid | Anti-islanding, power quality, protection settings, metering |
| SANS 10106 | Installation, Maintenance & Inspection of Emergency Lighting | Commercial buildings with >100 occupants | Duration (1hr/3hr), lux levels, test schedules |
| SANS 1507 | Electric Cables - PVC Insulated | Cable selection | Current carrying capacity tables, derating factors, voltage drop limits |
| OHS Act - Electrical Installation Regulations (2009) | Legal framework for all electrical work | ALL installations | Registered persons, COC requirements, notification, record keeping |
| Municipal Bylaws | Varies by municipality | Connection to municipal grid | Meter specs, connection application, SSEG registration, feed-in tariffs |

## A3. Pricing Engine Variables

The tool must account for these pricing variables to generate accurate, market-competitive quotations.

A3.1 Markup & Margin Structure

| Variable | Description | Typical Range | Formula |
| --- | --- | --- | --- |
| material_markup_pct | Markup on material cost price | 15% - 35% | sell_price = cost_price x (1 + markup_pct) |
| labour_rate_master | Daily rate for master electrician | R 2,200 - R 3,500/day | Based on region and experience level |
| labour_rate_assistant | Daily rate for electrical assistant | R 800 - R 1,500/day | Based on region |
| labour_rate_apprentice | Daily rate for registered apprentice | R 500 - R 900/day | Based on year of study |
| overhead_pct | Company overhead allocation | 8% - 15% | Applied to subtotal before VAT |
| profit_margin_pct | Net profit target | 10% - 25% | Applied after overhead |
| contingency_pct | Unforeseen work allowance | 5% - 10% | Applied to labour + materials subtotal |
| vat_rate | Current SA VAT rate | 15% | Applied to grand total |
| waste_factor_pct | Material waste allowance | 5% - 15% | Varies by material type: cable 8%, conduit 10%, fittings 5% |

A3.2 Cost Escalation Variables

| Variable | Description | 2026 Baseline | Update Frequency |
| --- | --- | --- | --- |
| cpi_annual | Consumer Price Index increase | 4.5% - 5.5% | Quarterly |
| copper_index | Copper commodity price (affects cable) | Volatile - track LME | Monthly |
| rand_usd_rate | Exchange rate (imported components) | R 18.20 - R 19.50 | Weekly |
| ppi_electrical | Producer Price Index - electrical equipment | 6% - 8% | Quarterly |
| steel_index | Steel price (affects DB boards, containment) | Track SAFAL/AMSA | Monthly |
| fuel_price | Diesel/petrol (affects transport/delivery) | R 22 - R 25/litre | Monthly |
| quote_validity_days | Period quote remains valid | 30 days standard | Per quote |

## A4. Labour Cost Model

Labour is typically 30-45% of total project cost. The tool must calculate labour accurately based on multiple factors.

A4.1 Labour Rate Per Point Method

| Point Type | Base Rate (ZAR) | Includes | Difficulty Multiplier Range |
| --- | --- | --- | --- |
| Light point - surface mount | R 280 - R 350 | Run cable, mount fitting, connect, test | 1.0x (standard) to 1.5x (high ceiling > 3m) |
| Light point - recessed/downlight | R 320 - R 420 | Cut hole, run cable, mount can, connect | 1.0x to 1.3x (concrete ceiling +30%) |
| Single socket outlet | R 300 - R 380 | Chase/mount box, run cable, connect, test | 1.0x to 1.8x (face brick +40%, concrete +80%) |
| Double socket outlet | R 320 - R 420 | Chase/mount box, run cable, connect, test | Same as single |
| Switch (1-4 lever) | R 180 - R 280 | Chase/mount box, run cable, connect | 1.0x to 1.5x |
| DB board installation | R 1,500 - R 4,500 | Mount, wire busbars, connect all circuits, label | Varies by size: 12-way to 48-way |
| Stove connection (3-phase) | R 1,200 - R 1,800 | Run 6mm2 cable, isolator, connect, test | 1.0x to 1.3x (distance > 15m) |
| Geyser connection | R 800 - R 1,500 | Run cable, install timer, isolator, connect | 1.0x to 1.5x (roof space difficulty) |
| AC connection | R 650 - R 1,200 | Run cable, isolator, disconnect, connect | 1.0x to 1.3x |
| Earth system | R 800 - R 1,500 | Drive spike, run earth conductor, test | 1.0x to 2.0x (rocky soil +50-100%) |
| Solar DB / changeover | R 2,500 - R 5,000 | Install solar DB, changeover switch, wire | Complexity-dependent |
| COC testing per circuit | R 150 - R 250 | Insulation, earth continuity, polarity, RCD trip | Based on accessibility |

A4.2 Labour Difficulty Multipliers

| Factor | Variable Name | Multiplier | Description |
| --- | --- | --- | --- |
| Standard new build (open walls) | diff_new_build | 1.0x | Cables laid before plastering, easy access |
| Renovation (chasing required) | diff_renovation | 1.4x - 1.8x | Chase walls, make good, dust extraction |
| Double storey ground floor | diff_double_ground | 1.0x | Standard ground floor access |
| Double storey upper floor | diff_double_upper | 1.15x - 1.3x | Vertical runs, working at height |
| Multi-storey (3+ floors) | diff_multi_storey | 1.2x - 1.5x | Riser runs, scaffolding, longer cable pulls |
| Face brick walls | diff_face_brick | 1.3x - 1.5x | Cannot chase, must use surface mount or conduit |
| Concrete walls/ceilings | diff_concrete | 1.5x - 2.0x | Diamond core drilling, SDS chasing |
| Ceiling height > 3m | diff_high_ceiling | 1.2x - 1.5x | Scaffolding or cherry picker required |
| Ceiling height > 6m | diff_very_high | 1.5x - 2.0x | Full scaffolding, safety harness, longer install time |
| Occupied premises | diff_occupied | 1.2x - 1.4x | Dust sheets, restricted hours, clean-up |
| Hazardous area (Zone 1/2) | diff_hazardous | 1.5x - 2.5x | Ex-rated equipment, special procedures |
| Roof space work | diff_roof_space | 1.2x - 1.4x | Confined space, heat, difficult access |
| Underground/trench work | diff_underground | 1.3x - 1.6x | Excavation, backfill, warning tape |

## A5. Regional Adjustment Factors

Material and labour costs vary significantly across South African regions. The tool must apply regional multipliers.

| Region / Metro | Labour Multiplier | Material Multiplier | Transport Add-on | Notes |
| --- | --- | --- | --- | --- |
| Gauteng (JHB/PTA) | 1.00x (base) | 1.00x (base) | R 0 - R 500 | Base pricing region, highest competition |
| Cape Town Metro | 1.05x - 1.15x | 1.02x - 1.05x | R 0 - R 500 | Higher living costs, strong demand |
| eThekwini (Durban) | 0.95x - 1.05x | 1.00x - 1.03x | R 0 - R 400 | Port proximity offsets some costs |
| Mpumalanga | 0.90x - 1.00x | 1.05x - 1.10x | R 500 - R 1,500 | Lower labour, higher delivery costs |
| Limpopo | 0.85x - 0.95x | 1.08x - 1.15x | R 800 - R 2,500 | Lower labour, significant transport premium |
| Free State | 0.88x - 0.95x | 1.05x - 1.12x | R 500 - R 1,800 | Limited supplier options, delivery delays |
| Eastern Cape (PE/EL) | 0.90x - 1.00x | 1.03x - 1.08x | R 400 - R 1,200 | Growing market, moderate transport |
| North West | 0.88x - 0.95x | 1.06x - 1.12x | R 600 - R 2,000 | Mining areas may command premium |
| Northern Cape | 0.85x - 0.95x | 1.10x - 1.20x | R 1,000 - R 3,500 | Remote, highest transport costs |
| Garden Route / rural | 0.95x - 1.10x | 1.05x - 1.15x | R 500 - R 2,000 | Holiday premium, seasonal demand |

## A6. Material Cost Database Structure

Each material item in the database must store the following fields for accurate pricing.

| Field Name | Data Type | Description | Example |
| --- | --- | --- | --- |
| item_code | STRING | Unique SKU / product code | CBi-QA120-C10 |
| item_description | STRING | Full product description | CBI QA 1P 10A C-curve MCB |
| category | ENUM | Product category | protection ¦ cable ¦ conduit ¦ socket ¦ switch ¦ fitting ¦ sundry |
| sub_category | STRING | Product sub-category | mcb ¦ elcb ¦ isolator ¦ surge_arrester |
| brand | STRING | Manufacturer / brand | CBI ¦ ABB ¦ Schneider ¦ Legrand ¦ Major Tech |
| unit | ENUM | Unit of measure | each ¦ metre ¦ roll ¦ length ¦ box ¦ kg |
| cost_price_excl | FLOAT | Supplier cost price excl VAT | R 145.00 |
| sell_price_excl | FLOAT | Calculated sell price excl VAT | R 188.50 |
| last_updated | DATE | Date price was last verified | 2026-02-01 |
| supplier | STRING | Primary supplier name | Radiant ¦ ARB ¦ Eurolux ¦ Magnet |
| lead_time_days | INTEGER | Standard delivery days | 1 - 14 |
| min_order_qty | INTEGER | Minimum order quantity | 1 ¦ 10 ¦ 100 |
| voltage_rating | STRING | Rated voltage | 230V ¦ 400V ¦ 525V |
| current_rating | STRING | Rated current (where applicable) | 10A ¦ 16A ¦ 20A ¦ 32A ¦ 63A |
| sans_approved | BOOLEAN | SABS/SANS approved | true ¦ false |
| nrcs_approved | BOOLEAN | NRCS LoA (Letter of Authority) | true ¦ false - CRITICAL for sockets, plugs, cables |

PART B: PRIORITY 1 - Commercial + Solar Installations

## B1. Commercial Electrical Parameters

B1.1 Commercial Project Input Variables

| Variable | Data Type | Options / Range | Why It Matters |
| --- | --- | --- | --- |
| occupancy_type | ENUM | office ¦ retail ¦ restaurant ¦ warehouse ¦ workshop ¦ medical ¦ education ¦ hospitality | Determines power density, lighting levels, emergency requirements |
| occupancy_count | INTEGER | 1 - 5,000 | Triggers SANS 10400-T fire requirements at >100 persons |
| operating_hours | ENUM | business_8to5 ¦ extended_12hr ¦ 24hr ¦ shift_work | Affects emergency lighting duration and UPS sizing |
| number_of_tenants | INTEGER | 1 - 50 | Determines sub-metering, separate DBs, tenant isolation |
| total_gfa_m2 | FLOAT | 50 - 100,000 | Primary driver for cable quantities, lighting counts, socket counts |
| server_room_present | BOOLEAN | true ¦ false | Dedicated circuits, UPS, cooling, fire suppression power |
| kitchen_type | ENUM | none ¦ kitchenette ¦ commercial_kitchen | Determines 3-phase requirements, extraction, dedicated circuits |
| hvac_type | ENUM | none ¦ split_units ¦ vrv_system ¦ central_chiller ¦ ducted | Electrical connection points, dedicated circuits, 3-phase supply |
| security_level | ENUM | basic ¦ standard ¦ high ¦ critical | CCTV power points, access control, alarm wiring allowance |
| data_requirements | ENUM | basic ¦ standard ¦ high_density ¦ data_centre | Data points per desk, server room, UPS requirements |
| backup_power | ENUM | none ¦ ups_only ¦ generator ¦ generator_ups ¦ solar_hybrid | Changeover switch, ATS, generator connection, fuel supply |
| fire_system_type | ENUM | none ¦ detection_only ¦ detection_suppression ¦ addressable | Fire panel power, detector wiring, sounder circuits |
| lift_elevator | BOOLEAN + COUNT | true ¦ false, count 1-8 | Dedicated 3-phase supply per lift, fireman switch |
| signage_power | ENUM | none ¦ basic ¦ illuminated ¦ digital | Dedicated circuits for external and internal signage |
| parking_bays | INTEGER | 0 - 500 | Parking lighting, EV charger pre-wire, boom gate power |
| ev_charger_provision | ENUM | none ¦ pre_wire ¦ install_7kw ¦ install_22kw | Dedicated circuits, sub-metering, cable sizing |

B1.2 Commercial Power Density Standards (SANS 10400-XA)

| Space Type | Lighting (W/m2) | Small Power (W/m2) | HVAC (W/m2) | Total Design Load (W/m2) |
| --- | --- | --- | --- | --- |
| Open plan office | 10 - 12 | 15 - 25 | 60 - 100 | 85 - 137 |
| Private office | 10 - 12 | 15 - 20 | 60 - 80 | 85 - 112 |
| Boardroom / meeting | 10 - 14 | 10 - 15 | 70 - 100 | 90 - 129 |
| Reception / lobby | 8 - 15 | 5 - 10 | 50 - 80 | 63 - 105 |
| Server / comms room | 8 - 10 | 500 - 2,000 | 200 - 800 | 708 - 2,810 |
| Kitchen / canteen | 10 - 12 | 30 - 100 | 80 - 120 | 120 - 232 |
| Retail shop | 15 - 25 | 10 - 20 | 50 - 100 | 75 - 145 |
| Restaurant / cafe | 8 - 15 | 20 - 50 | 80 - 120 | 108 - 185 |
| Warehouse / storage | 5 - 8 | 2 - 5 | 10 - 30 | 17 - 43 |
| Workshop / light industrial | 10 - 15 | 20 - 80 | 30 - 60 | 60 - 155 |
| Bathroom / WC | 8 - 10 | 5 - 8 | 20 - 40 | 33 - 58 |
| Corridor / circulation | 5 - 8 | 2 - 5 | 15 - 30 | 22 - 43 |
| Parking (covered) | 2 - 5 | 1 - 2 | 5 - 15 | 8 - 22 |

B1.3 Commercial Phase Balancing

Three-phase commercial installations MUST be phase-balanced. The tool should auto-allocate circuits across L1, L2, L3 and flag imbalances exceeding 10%.

| Parameter | Requirement | Tool Implementation |
| --- | --- | --- |
| Maximum phase imbalance | < 10% between any two phases (SANS 10142) | Calculate kW per phase, warn if > 10% difference |
| Neutral current calculation | Must account for harmonic loads (IT equipment) | I_neutral = sqrt(I_L1^2 + I_L2^2 + I_L3^2 - I_L1.I_L2 - I_L2.I_L3 - I_L1.I_L3) |
| Circuit allocation | Distribute evenly across phases | Auto-assign circuits to phases, allow manual override |
| Maximum demand calculation | Apply diversity factors per SANS 10142 Table B.1 | Total_demand = sum(circuit_load x diversity_factor) |
| Diversity factor - lighting | 0.75 for > 10 circuits | Reduce total lighting load by 25% |
| Diversity factor - sockets | 0.4 for general, 1.0 for dedicated | General sockets at 40%, dedicated at 100% |
| Diversity factor - HVAC | 0.8 for multiple units | Stagger start-up loads |
| Diversity factor - cooking | 0.6 for commercial kitchens | Multiple appliances rarely all at peak simultaneously |

## B2. Solar PV System Parameters

Solar installations are the fastest-growing segment. The tool must handle these specific parameters.

B2.1 Solar System Input Variables

| Variable | Data Type | Options / Range | Calculation Impact |
| --- | --- | --- | --- |
| system_size_kwp | FLOAT | 1 - 1,000 kWp | Determines panel count, inverter size, cable sizing |
| panel_wattage | INTEGER | 400 - 615 Wp | Panels_needed = system_size_kwp x 1000 / panel_wattage |
| panel_type | ENUM | mono_perc ¦ mono_topcon ¦ bifacial ¦ thin_film | Affects efficiency, cost per watt, mounting requirements |
| inverter_type | ENUM | string ¦ micro ¦ hybrid ¦ off_grid | Determines AC/DC wiring, protection, monitoring |
| inverter_size_kw | FLOAT | 1 - 500 kW | Must match or exceed system_size_kwp (DC:AC ratio 1.0-1.3) |
| inverter_phases | ENUM | single_phase ¦ three_phase | Affects connection to DB, protection, and grid feed-in |
| roof_type | ENUM | IBR ¦ corrugated ¦ concrete_flat ¦ tile ¦ kliplock | Determines mounting system, waterproofing, and labour |
| roof_orientation | ENUM | north ¦ north_east ¦ north_west ¦ east ¦ west ¦ flat | Affects yield calculation and tilt angle recommendation |
| roof_tilt_degrees | FLOAT | 0 - 45 | Optimal for Pretoria: 25-30 degrees north-facing |
| roof_area_m2 | FLOAT | 10 - 10,000 | Limits maximum system size (approx 5-7 m2 per kWp) |
| annual_consumption_kwh | FLOAT | 3,000 - 5,000,000 | Used to size system and calculate payback period |
| current_tariff_r_kwh | FLOAT | R 1.50 - R 4.50 | Revenue/saving calculation for ROI |
| feed_in_tariff_r_kwh | FLOAT | R 0.00 - R 1.50 | Municipality-dependent, affects grid export revenue |
| grid_connection | ENUM | grid_tied ¦ hybrid ¦ off_grid | Determines protection scheme and battery requirements |
| sseg_registration | BOOLEAN | true ¦ false | Required for grid-tied systems, affects compliance cost |
| module_string_length | INTEGER | 6 - 20 | Determined by inverter MPPT voltage window |
| number_of_mppt | INTEGER | 1 - 12 | Inverter MPPT inputs for string configuration |
| dc_cable_size_mm2 | ENUM | 4 ¦ 6 ¦ 10 | Based on string current and cable run length |
| ac_cable_size_mm2 | ENUM | 2.5 ¦ 4 ¦ 6 ¦ 10 ¦ 16 ¦ 25 ¦ 35 | Based on inverter output current and distance to DB |

B2.2 Solar Component Pricing (2026 ZAR Baseline)

| Component | Specification | Price Range (excl VAT) | Notes |
| --- | --- | --- | --- |
| Solar panel 550-580W | Tier 1 mono PERC | R 1,800 - R 2,800 each | Canadian Solar, JA Solar, Longi, Trina |
| Solar panel 580-615W | Tier 1 TopCon/bifacial | R 2,200 - R 3,500 each | Premium efficiency, better low-light performance |
| String inverter 5kW (1-ph) | Grid-tied | R 12,000 - R 18,000 | Deye, Sungrow, Goodwe, SMA |
| String inverter 8-12kW (3-ph) | Grid-tied | R 18,000 - R 35,000 | Sungrow, Huawei, SMA, Fronius |
| Hybrid inverter 5kW (1-ph) | Battery compatible | R 18,000 - R 28,000 | Deye, Sunsynk, Victron |
| Hybrid inverter 8-12kW (3-ph) | Battery compatible | R 30,000 - R 55,000 | Deye, Sunsynk, Victron |
| Commercial inverter 50-100kW | 3-phase string | R 60,000 - R 150,000 | Huawei, Sungrow, SMA |
| Mounting (IBR roof) | Rail + clamp system | R 800 - R 1,500 per panel | K2, Schletter, local |
| Mounting (flat roof / tilt) | Ballasted or fixed tilt | R 1,200 - R 2,500 per panel | Higher due to tilt frames, wind load |
| DC cable 6mm2 (solar) | Double insulated, UV rated | R 18 - R 28 per metre | Must be TUV certified for solar |
| AC cable (varies) | SANS 1507 rated | R 18 - R 185 per metre | Size depends on inverter output |
| DC isolator | Rated for 600/1000V DC | R 450 - R 850 | Required at panel array and inverter |
| AC isolator | Rated for 230/400V AC | R 250 - R 600 | Required at inverter and DB |
| Surge protection (DC) | Type 2 SPD, 600/1000V | R 800 - R 1,800 | Required on DC side |
| Surge protection (AC) | Type 2 SPD, 230/400V | R 600 - R 1,200 | Required on AC side |
| Solar DB board | Dedicated solar distribution | R 1,500 - R 3,500 | Separate from main DB |
| Changeover switch (manual) | 63A - 100A | R 1,200 - R 3,500 | For non-grid-tied backup |
| ATS (automatic transfer) | 63A - 100A | R 3,500 - R 12,000 | Automatic grid/solar/battery switching |
| Solar installation labour | Per kWp installed | R 1,500 - R 3,000 per kWp | Includes mechanical + electrical |
| SSEG registration | Municipal application | R 0 - R 9,000 | Eskom: free for <50kVA until Mar 2026 |
| Solar COC | Separate from building COC | R 2,500 - R 5,000 | Required for all solar installations |

## B3. Battery Storage Parameters

| Variable | Data Type | Options / Range | Notes |
| --- | --- | --- | --- |
| battery_required | BOOLEAN | true ¦ false | Determines if storage component is included |
| battery_chemistry | ENUM | lfp ¦ nmc ¦ lead_acid | LFP preferred for SA (heat tolerance, cycle life) |
| battery_capacity_kwh | FLOAT | 5 - 500 kWh | Sized based on backup requirement or self-consumption target |
| battery_brand | ENUM | byd ¦ pylontech ¦ freedom_won ¦ hubble ¦ dyness | Affects warranty, compatibility, pricing |
| depth_of_discharge | FLOAT | 80% - 95% | Usable capacity = total_kwh x DoD |
| backup_duration_hours | FLOAT | 2 - 24 | Hours of backup at average load |
| essential_load_kw | FLOAT | 1 - 50 | Load that must run during outage |
| battery_location | ENUM | indoor ¦ outdoor ¦ garage ¦ battery_room | Affects enclosure, ventilation, IP rating requirements |

B3.1 Battery Pricing (2026 ZAR)

| Battery | Capacity | Price Range (excl VAT) | Cycle Life |
| --- | --- | --- | --- |
| Pylontech US3000C | 3.55 kWh (stackable) | R 16,000 - R 20,000 | 6,000+ cycles at 80% DoD |
| Pylontech US5000 | 4.84 kWh (stackable) | R 22,000 - R 28,000 | 6,000+ cycles at 80% DoD |
| BYD HVS 5.1 | 5.12 kWh (stackable) | R 28,000 - R 35,000 | 10,000 cycles at 90% DoD |
| BYD HVM 8.3 | 8.28 kWh (stackable) | R 42,000 - R 55,000 | 10,000 cycles at 90% DoD |
| Freedom Won Lite Home 5/4 | 5.12 kWh | R 30,000 - R 38,000 | 5,000 cycles at 80% DoD |
| Freedom Won Lite Home 10/8 | 10.24 kWh | R 55,000 - R 70,000 | 5,000 cycles at 80% DoD |
| Hubble AM-2 | 5.12 kWh | R 18,000 - R 24,000 | 6,000 cycles at 80% DoD |
| Hubble AM-5 | 5.32 kWh | R 20,000 - R 26,000 | 6,000 cycles at 80% DoD |
| Dyness B4850 | 4.8 kWh (stackable) | R 16,000 - R 22,000 | 6,000 cycles at 80% DoD |

## B4. SSEG Compliance Variables (NRS 097)

All grid-connected solar systems must comply with NRS 097-2-3 and municipal SSEG bylaws.

| Requirement | Parameter | Standard / Threshold | Tool Implementation |
| --- | --- | --- | --- |
| Anti-islanding protection | Relay type and settings | NRS 097-2-3 Table 1 | Auto-include anti-islanding relay or inverter with built-in protection |
| Maximum export capacity | Export limit kW | As per municipal approval (often 0 for residential) | Include export limiter if required, or zero-export CT |
| Power quality - voltage | Grid voltage range | 230V +10% / -15% (207V to 253V) | Inverter must disconnect outside range |
| Power quality - frequency | Grid frequency range | 50Hz +/- 2.5% (48.75 - 51.25 Hz) | Inverter must disconnect outside range |
| Power factor | Minimum power factor | > 0.95 leading or lagging | Inverter setting, reactive power compensation |
| Protection settings | Over/under voltage, frequency | Per NRS 097-2-3 Table 3 | Pre-configure inverter protection settings |
| Metering | Bidirectional meter | Required for feed-in tariff | Include bi-directional meter cost if grid export |
| Zero export device | CT clamp or power meter | Required if no feed-in allowed | Auto-include for municipalities without feed-in tariff |
| Earthing | Additional earth electrode | May be required for inverter | Include earth spike at inverter location |
| Signage | Solar warning labels | Mandatory on DB, inverter, meter box | Include signage kit cost (R 200 - R 500) |
| Documentation | Single line diagram + design report | Required for SSEG application | Auto-generate SLD, include in quotation |
| Municipal application fee | Varies by municipality | R 0 (Eskom <50kVA) to R 9,000+ | Look up by municipality ENUM |

B5. Commercial-Specific Standards Checklist

The tool should auto-include these items when project_type = commercial:

| Requirement | Standard | Trigger Condition | Cost Allowance |
| --- | --- | --- | --- |
| Emergency lighting | SANS 10106 | occupancy_count > 100 OR commercial building | R 350 - R 800 per fitting + battery pack |
| Exit signs (illuminated) | SANS 10400-T | All commercial buildings | R 450 - R 1,200 each |
| Fire detection panel | SANS 10139 | All commercial buildings > 250m2 | R 8,000 - R 45,000 depending on zones |
| Smoke / heat detectors | SANS 10139 | Per room / zone coverage | R 250 - R 600 each (wired) |
| Manual call points | SANS 10139 | At every exit door | R 350 - R 600 each |
| Sounders / strobes | SANS 10139 | Coverage per floor | R 400 - R 800 each |
| Disability provisions | SANS 10400-S | All public buildings | Tactile exits, visual alarms, accessible switches at 1m height |
| 3-phase balance verification | SANS 10142 | All 3-phase installations | Include in testing scope |
| Maximum demand calculation | SANS 10142 Annex B | All installations | Auto-calculate and include in design docs |
| As-built drawings | SANS 10142 | All installations > 100A | R 2,500 - R 8,000 depending on complexity |
| Maintenance schedule | OHS Act | All commercial installations | Include template maintenance plan |
| Earthing report | SANS 10142 / SANS 62305 | All commercial installations | Earth resistance test, include in COC |

PART C: PRIORITY 2 - Residential New Builds

## C1. Dwelling Classification

| Variable | Data Type | Options / Range | Impact |
| --- | --- | --- | --- |
| dwelling_type | ENUM | rdp ¦ townhouse ¦ simplex ¦ duplex ¦ freestanding ¦ cluster ¦ estate | Determines base point counts and circuit complexity |
| bedrooms | INTEGER | 1 - 8 | Light points, sockets, circuit count |
| bathrooms | INTEGER | 1 - 5 | Extractor fans, shaver sockets, light points, earth bonding |
| living_areas | INTEGER | 1 - 4 | Lounge, dining, family room - socket density |
| kitchen_count | INTEGER | 1 - 2 | Dedicated circuits, stove, oven, dishwasher, extraction |
| garage_count | INTEGER | 0 - 3 | Motor points, high-power outlets, lighting |
| laundry_room | BOOLEAN | true ¦ false | Washing machine, tumble dryer dedicated circuits |
| home_office | BOOLEAN | true ¦ false | Extra sockets, data points, dedicated circuit |
| outdoor_entertainment | ENUM | none ¦ basic ¦ braai_area ¦ full_outdoor_kitchen | Outdoor sockets, lighting, extraction |
| pool | BOOLEAN | true ¦ false | Pool pump circuit, pool light (12V transformer), timer |
| borehole | BOOLEAN | true ¦ false | Borehole pump circuit, pressure switch |
| boundary_wall_type | ENUM | none ¦ wall ¦ palisade ¦ electric_fence | Electric fence energizer circuit, gate motor |
| gate_type | ENUM | none ¦ swing ¦ sliding | Gate motor connection, intercom wiring |
| alarm_prewire | BOOLEAN | true ¦ false | Alarm power supply, zone wiring allowance |
| solar_ready | BOOLEAN | true ¦ false | Spare ways in DB, conduit to roof, changeover space |
| ev_ready | BOOLEAN | true ¦ false | Dedicated 32A circuit to garage, cable sizing for future EV charger |

## C2. Room-by-Room Electrical Requirements

This is the core of the residential quotation engine. Each room type has standard electrical requirements per SANS 10142.

C2.1 Minimum Requirements per Room Type

| Room Type | Min Light Points | Min Socket Outlets | Switches | Dedicated Circuits | Extras |
| --- | --- | --- | --- | --- | --- |
| Main bedroom | 1 ceiling + 2 bedside | 3 double (min) | 1x 2-lever + 2-way | None standard | Dimmer option, AC pre-wire |
| Secondary bedroom | 1 ceiling | 2 double | 1x 1-lever | None | Data point optional |
| En-suite bathroom | 1 ceiling (IP44) | 1 shaver socket | 1x 1-lever | Extractor fan | Underfloor heating point, earth bonding |
| Main bathroom | 1 ceiling (IP44) | 1 shaver socket | 1x 1-lever | Extractor fan | Earth bonding of all metal pipes |
| Guest WC | 1 ceiling (IP44) | 0 - 1 shaver | 1x 1-lever | Extractor optional | IP rating if < 2.4m from bath/shower |
| Kitchen | 2 ceiling + 1 counter | 4 double counter + 2 wall | 2x multi-lever | Stove (32A 3-ph), oven, dishwasher, fridge, microwave | Extractor fan point, waste disposal point |
| Scullery / laundry | 1 ceiling | 2 double | 1x 1-lever | Washing machine (16A), tumble dryer (16A) | Iron point on wall |
| Lounge | 1 ceiling + 2 wall wash | 4 double (min) | 1x 2-lever + 2-way | None standard | TV point, dimmer, surround sound pre-wire |
| Dining room | 1 ceiling (pendant) | 2 double | 1x 1-lever + dimmer | None | Dimmer recommended |
| Family room / TV room | 1 ceiling | 3 double | 1x 1-lever | None | TV point, surround sound |
| Study / home office | 1 ceiling + 1 desk lamp | 3 double + 1 USB combo | 1x 1-lever | Dedicated 16A circuit | Data point, UPS point |
| Corridor / passage | 1 per 3m length | 1 double per 6m | 2-way switching both ends | None | PIR sensor option, night light |
| Entrance / foyer | 1 ceiling + 1 wall | 1 double | 2-way switching | None | PIR sensor, intercom unit |
| Garage (single) | 1 ceiling + 1 workbench | 2 double + 1 x 15A red | 1x 1-lever | Gate motor (if applicable) | PIR security light |
| Garage (double) | 2 ceiling + 1 workbench | 3 double + 1 x 15A red | 1x 2-lever | Gate motor | PIR security light, EV pre-wire |
| Outdoor (front) | 1-2 wall mounted | 1 weatherproof | Inside switch | None | PIR sensor, house number light |
| Outdoor (rear) | 1-2 wall + 1 braai area | 1-2 weatherproof | Inside switch | Pool pump if applicable | Garden spike lights, water feature point |
| Pool area | 1 pool light (12V) | 1 weatherproof (>3.5m from pool) | Inside switch | Pool pump 16A, chlorinator | 12V transformer, timer, earth bonding |

## C3. Circuit Design Parameters (SANS 10142)

The tool must auto-design the circuit schedule based on room inputs.

C3.1 Circuit Rules

| Rule | SANS 10142 Requirement | Tool Logic |
| --- | --- | --- |
| Max points per lighting circuit | 12 points maximum (recommended 8-10) | Count light points, split into circuits of max 10 |
| Max sockets per circuit | No fixed limit, but max 16A total load | Calculate total socket load, recommend max 8 doubles per circuit |
| Earth leakage protection | All circuits must be protected by 30mA ELCB | Auto-include 30mA ELCB for every circuit group |
| Dedicated circuit requirement | Appliances > 2kW must have dedicated circuit | Flag stove, geyser, AC, pool pump, borehole as dedicated |
| Circuit breaker rating | Must be <= cable current capacity | Match MCB to cable: 1.5mm=10A, 2.5mm=16A/20A, 4mm=25A, 6mm=32A |
| Cable sizing - voltage drop | Max 5% voltage drop from DB to furthest point | Calculate: Vdrop = 2 x L x I x R / 1000 (must be < 11.5V for 230V) |
| Cable sizing - current | Per SANS 1507 / IEC 60364 | Derate for grouping, insulation type, ambient temperature |
| Neutral conductor | Same size as phase conductor (single phase) | Auto-match neutral to phase cable size |
| Earth conductor | Min 2.5mm CPC for power, 1.5mm for lighting | Auto-size earth conductor per circuit |
| Ring vs radial | Radial circuits standard in SA (not ring) | All circuits designed as radial (not UK-style ring) |
| Spare ways in DB | Minimum 2 spare ways recommended | Add 15-20% spare ways to calculated total |
| Separation of essential/non-essential | Recommended for solar/generator backup | Create two groups: essential (lights, fridge, alarm) and non-essential |

C3.2 Cable Selection Table

| Cable Size (mm2) | Max MCB (A) | Current Capacity (clipped) | Typical Use | Voltage Drop (mV/A/m) | Cost per metre (2026) |
| --- | --- | --- | --- | --- | --- |
| 1.5mm2 2-core + E | 10A | 14.5A | Lighting circuits | 29.0 | R 12 - R 18 |
| 2.5mm2 2-core + E | 16A / 20A | 20.0A | General socket outlets | 17.4 | R 18 - R 28 |
| 4mm2 2-core + E | 25A | 27.0A | High-load sockets, AC | 10.9 | R 28 - R 42 |
| 6mm2 2-core + E | 32A | 34.0A | Stove, large AC, sub-DB feed | 7.3 | R 42 - R 65 |
| 10mm2 2-core + E | 40A - 50A | 46.0A | Sub-DB feed, geyser bank | 4.4 | R 65 - R 95 |
| 16mm2 2-core + E | 63A | 61.0A | Main feed, large sub-DB | 2.8 | R 95 - R 145 |
| 25mm2 (single core x4) | 80A | 80.0A | Main supply, 3-phase feed | 1.75 | R 45 - R 75 per core |
| 6mm2 4-core (3-ph) | 32A | 34.0A per phase | 3-phase stove, 3-phase AC | 7.3 | R 65 - R 95 |
| 10mm2 4-core (3-ph) | 40A | 46.0A per phase | 3-phase sub-DB feed | 4.4 | R 95 - R 140 |

C3.3 Derating Factors (SANS 1507 / IEC 60364)

| Factor | Condition | Derating Multiplier | Applied To |
| --- | --- | --- | --- |
| Grouping (2 circuits) | 2 cables touching | 0.80 | Current capacity |
| Grouping (3 circuits) | 3 cables in same conduit | 0.70 | Current capacity |
| Grouping (4-6 circuits) | 4-6 cables grouped | 0.57 - 0.65 | Current capacity |
| Grouping (7-12 circuits) | 7+ cables in same trunking | 0.50 - 0.54 | Current capacity |
| Ambient temp 35C | Standard SA summer | 0.94 | Current capacity |
| Ambient temp 40C | Hot roof space / ceiling | 0.87 | Current capacity |
| Ambient temp 45C | Direct sun on conduit | 0.79 | Current capacity |
| Ambient temp 50C | Engine room / near machinery | 0.71 | Current capacity |
| Thermal insulation (one side) | Cable touching insulation | 0.75 | Current capacity |
| Thermal insulation (enclosed) | Cable enclosed in insulation | 0.50 | Current capacity |
| Underground (direct buried) | In ground at 0.5m depth | Per SANS 1507 Table | Use underground cable type |
| Harmonic current (33%+) | IT equipment / LED drivers | 0.86 | Neutral conductor sizing |

## C4. Dedicated Circuit Specifications

These are high-value line items that are frequently missing from basic quotation tools.

| Appliance | Circuit Rating | Cable Size | Protection | Additional Components | Estimated Cost (installed) |
| --- | --- | --- | --- | --- | --- |
| Electric stove (3-ph) | 32A per phase | 6mm2 4-core | 3-pole 32A MCB | Stove isolator 32A, stove cable 1.5m | R 3,000 - R 4,500 |
| Electric stove (1-ph) | 32A | 6mm2 2C+E | 1-pole 32A MCB | Stove isolator 32A, stove cable | R 2,200 - R 3,500 |
| Electric oven (built-in) | 20A | 2.5mm2 2C+E | 20A MCB | Isolator switch, flex connection | R 1,500 - R 2,500 |
| Geyser (150L) | 20A | 2.5mm2 2C+E | 20A MCB + dedicated 30mA ELCB | Geyser isolator, timer, drip tray | R 1,800 - R 3,000 |
| Geyser (200L) | 20A | 4mm2 2C+E | 20A MCB + dedicated 30mA ELCB | Geyser isolator, timer, drip tray | R 2,000 - R 3,500 |
| Air conditioner (split) | 16A - 20A | 2.5mm2 - 4mm2 | 16A/20A MCB | AC isolator (outdoor), drain point | R 1,200 - R 2,500 |
| Dishwasher | 16A | 2.5mm2 2C+E | 16A MCB | Switched socket outlet near unit | R 800 - R 1,200 |
| Washing machine | 16A | 2.5mm2 2C+E | 16A MCB | Switched socket outlet | R 800 - R 1,200 |
| Tumble dryer | 16A | 2.5mm2 2C+E | 16A MCB | Switched socket outlet, vent point | R 800 - R 1,200 |
| Pool pump | 16A | 2.5mm2 2C+E | 16A MCB + 30mA ELCB | Timer, isolator, weatherproof encl. | R 1,500 - R 2,800 |
| Borehole pump | 16A - 32A | 2.5mm2 - 6mm2 | MCB + ELCB | Starter, pressure switch, float | R 2,500 - R 5,000 |
| Gate motor | 10A | 1.5mm2 2C+E | 10A MCB | Transformer, battery backup, intercom | R 1,200 - R 2,500 |
| Electric fence | 10A | 1.5mm2 2C+E | 10A MCB | Energizer, battery backup | R 800 - R 1,500 |
| Underfloor heating | 16A - 32A | 2.5mm2 - 6mm2 | Sized to mat | Thermostat, sensor probe | R 1,500 - R 4,000 |
| EV charger (7kW) | 32A | 6mm2 2C+E | 32A MCB + Type A ELCB | Dedicated EV circuit, charger unit | R 8,000 - R 18,000 |
| EV charger (22kW 3-ph) | 32A per phase | 6mm2 4-core | 3-pole 32A + Type B ELCB | Dedicated 3-ph circuit, charger | R 18,000 - R 35,000 |
| Solar inverter (5kW 1-ph) | 25A - 32A | 4mm2 - 6mm2 | MCB + ELCB | Solar DB, DC isolator, signage | R 2,500 - R 4,000 (excl inverter) |
| Jacuzzi / hot tub | 32A | 6mm2 2C+E | 32A MCB + 30mA ELCB | Isolator, bonding, GFCI | R 2,500 - R 4,000 |

C5. Residential-Specific Standards Checklist

| Requirement | Standard Reference | Detail | Cost Impact |
| --- | --- | --- | --- |
| Smoke detectors | SANS 10400-T / NBR | Min 1 per floor + every bedroom corridor | R 180 - R 350 each (battery) or R 350 - R 600 (wired) |
| Socket height from floor | SANS 10142-1 Cl 6.3 | Min 150mm from finished floor level | Layout compliance check |
| Bathroom zones | SANS 10142-1 Cl 6.13 | Zone 0/1/2 restrictions on socket and fitting placement | Must use IP44+ fittings in Zone 1, no sockets in Zone 0/1 |
| Earth bonding (bathroom) | SANS 10142-1 Cl 6.13 | All metal pipes and fittings bonded to earth | R 300 - R 600 per bathroom |
| RCD protection | SANS 10142-1 Cl 7.2 | All circuits protected by max 30mA RCD | Include in DB board pricing |
| DB board location | SANS 10142-1 Cl 6.5 | Inside building, accessible, min 1.5m from ground | Affects cable run lengths |
| Cable routing | SANS 10142-1 Cl 6.7 | Vertical and horizontal zones only | No diagonal runs - affects cable quantities |
| Outdoor socket IP rating | SANS 10142-1 Cl 6.14 | Minimum IP55 for outdoor installations | R 250 - R 500 for weatherproof outlets |
| Prepaid meter ready board | Municipal bylaws | Tshwane/JHB/eThekwini specific requirements | R 800 - R 2,500 installed |
| As-built drawings | SANS 10142-1 | Required for all new installations | R 1,500 - R 3,500 depending on house size |
| SANS 10400-XA compliance | Energy regulations | Hot water system efficiency, lighting W/m2 limits | May require timer, solar geyser, LED-only specification |

PART D: PRIORITY 3 - Maintenance & COC Renewals

## D1. COC Inspection Parameters

A Certificate of Compliance inspection is required for every change of property ownership, new installation, or alteration. This is a high-volume, recurring revenue stream.

D1.1 COC Inspection Input Variables

| Variable | Data Type | Options / Range | Pricing Impact |
| --- | --- | --- | --- |
| inspection_reason | ENUM | new_installation ¦ alteration ¦ property_sale ¦ landlord_compliance ¦ insurance ¦ periodic | Determines scope and documentation |
| property_type | ENUM | residential ¦ commercial ¦ industrial ¦ mixed_use | Determines testing scope and standards |
| property_size_m2 | FLOAT | 20 - 100,000 | Affects time on site, number of circuits to test |
| number_of_db_boards | INTEGER | 1 - 20 | Each DB requires full inspection |
| total_circuits | INTEGER | 3 - 200 | Primary driver of inspection time |
| supply_type | ENUM | single_phase ¦ three_phase | 3-phase requires additional phase rotation and balance tests |
| installation_age_years | INTEGER | 0 - 50+ | Older installations more likely to have defects |
| previous_coc_available | BOOLEAN | true ¦ false | Comparison baseline, affects inspection approach |
| solar_system_present | BOOLEAN | true ¦ false | Requires additional SSEG-specific tests |
| generator_present | BOOLEAN | true ¦ false | Requires changeover switch and interlock testing |
| swimming_pool | BOOLEAN | true ¦ false | Requires earth bonding and RCD testing |
| access_limitations | ENUM | full ¦ partial_ceiling ¦ partial_db ¦ limited | Affects inspection time and report caveats |

D1.2 COC Inspection Pricing Model

| Property Type | Base Inspection Fee | Per Additional Circuit | Per Additional DB | Re-inspection Fee |
| --- | --- | --- | --- | --- |
| Small residential (< 100m2) | R 1,200 - R 1,800 | R 80 - R 120 | R 500 - R 800 | R 600 - R 900 |
| Medium residential (100-250m2) | R 1,800 - R 2,800 | R 80 - R 120 | R 500 - R 800 | R 800 - R 1,200 |
| Large residential (250-500m2) | R 2,800 - R 4,500 | R 80 - R 120 | R 500 - R 800 | R 1,200 - R 1,800 |
| Estate / luxury (> 500m2) | R 4,500 - R 8,000 | R 100 - R 150 | R 600 - R 1,000 | R 1,500 - R 2,500 |
| Small commercial (< 200m2) | R 2,500 - R 4,000 | R 100 - R 150 | R 600 - R 1,000 | R 1,200 - R 1,800 |
| Medium commercial (200-1000m2) | R 4,000 - R 8,000 | R 120 - R 180 | R 800 - R 1,200 | R 1,800 - R 3,000 |
| Large commercial (> 1000m2) | R 8,000 - R 20,000 | R 150 - R 250 | R 1,000 - R 1,500 | R 3,000 - R 6,000 |
| Industrial premises | R 6,000 - R 25,000+ | R 150 - R 300 | R 1,000 - R 2,000 | R 3,000 - R 8,000 |

## D2. Defect Classification & Remedial Pricing

When a COC inspection fails, the tool must generate a remedial works quotation. Defects are classified by severity.

D2.1 Defect Severity Classification

| Severity | Classification | Definition | Action Required | COC Impact |
| --- | --- | --- | --- | --- |
| Critical | Immediate danger | Risk of electrocution, fire, or explosion | Must be rectified before COC can be issued | FAIL - no COC |
| Major | Non-compliant | Does not meet SANS 10142 but not immediately dangerous | Must be rectified for COC | FAIL - no COC |
| Minor | Advisory | Best practice recommendation, does not prevent COC | Recommended improvement, noted in report | PASS with notes |

D2.2 Common Defects & Remedial Pricing

| Defect | Severity | SANS 10142 Reference | Typical Remedial Cost | Frequency (% of inspections) |
| --- | --- | --- | --- | --- |
| No earth leakage (ELCB) protection | Critical | Cl 7.2.6 | R 950 - R 1,800 (install ELCB) | 15-20% |
| Earth leakage not tripping < 30mA | Critical | Cl 7.2.6 | R 950 - R 1,800 (replace ELCB) | 10-15% |
| Exposed live conductors | Critical | Cl 6.2 | R 200 - R 800 (repair/enclose) | 5-10% |
| No earth connection / broken earth | Critical | Cl 6.11 | R 800 - R 2,500 (install earth system) | 8-12% |
| DB board in poor condition | Major | Cl 6.5 | R 3,500 - R 12,000 (replace DB) | 10-15% |
| Incorrect cable sizing | Major | Cl 6.7 | R 500 - R 5,000 (re-cable) | 5-8% |
| No isolator on geyser | Major | Cl 6.10 | R 350 - R 600 (install isolator) | 20-25% |
| Geyser not on dedicated circuit | Major | Cl 6.10 | R 1,500 - R 3,000 (run dedicated) | 10-15% |
| Incorrect polarity | Major | Cl 6.2 | R 200 - R 500 per point (re-wire) | 5-8% |
| Non-compliant bathroom installation | Major | Cl 6.13 | R 500 - R 3,000 (relocate/IP rate) | 8-12% |
| Missing circuit breakers / wrong rating | Major | Cl 7.2 | R 150 - R 400 per MCB | 10-15% |
| Poor connections in DB | Major | Cl 6.5 | R 500 - R 2,000 (re-terminate) | 15-20% |
| Unlabelled circuits | Minor | Cl 6.5 | R 200 - R 500 (label all) | 30-40% |
| No surge protection | Minor | Advisory | R 800 - R 1,800 (install SPD) | 60-70% |
| Missing blanking plates on DB | Minor | Cl 6.5 | R 50 - R 150 | 20-30% |
| No smoke detectors | Minor | SANS 10400-T | R 200 - R 600 per unit | 40-50% |
| Extension cords as permanent wiring | Major | Cl 6.2 | R 500 - R 2,000 (install points) | 10-15% |
| Overloaded circuits | Major | Cl 7.2 | R 1,500 - R 4,000 (add circuits) | 8-12% |

## D3. Testing Equipment & Required Procedures

The tool should reference these tests when generating COC inspection quotations and ensure all are included.

D3.1 Mandatory Tests (SANS 10142-1 Section 8)

| Test | Instrument | Pass Criteria | SANS 10142 Reference | Approximate Time per Circuit |
| --- | --- | --- | --- | --- |
| Visual inspection | Eyes + torch | No visible defects, correct installation methods | Cl 8.2 | 2-5 min per area |
| Earth continuity | Earth loop impedance tester | < 1 ohm (residential), < 0.5 ohm (commercial) | Cl 8.4.2 | 1-2 min per circuit |
| Insulation resistance | Insulation resistance tester (500V DC) | > 1 M-ohm between all conductors | Cl 8.4.3 | 2-3 min per circuit |
| Polarity check | Polarity tester / socket tester | Correct L-N-E at all points | Cl 8.4.4 | 30 sec per point |
| Earth fault loop impedance | Loop impedance tester | Zs < value for MCB type/rating (Table 8.1) | Cl 8.4.5 | 1-2 min per circuit |
| RCD / ELCB trip test | RCD tester | Trips within 300ms at rated current (30mA) | Cl 8.4.6 | 30 sec per device |
| RCD trip time at 5x rated | RCD tester | Trips within 40ms at 150mA (for 30mA device) | Cl 8.4.6 | 30 sec per device |
| Prospective fault current | PFC meter | < rated breaking capacity of MCBs | Cl 8.4.7 | 1 min at DB |
| Phase rotation (3-ph only) | Phase rotation meter | Correct sequence L1-L2-L3 | Cl 8.4.8 | 1 min at DB |
| Voltage measurement | Multimeter | 230V +10/-15% (207V - 253V) | Cl 8.4.1 | 1 min at DB |
| Earth electrode resistance | Earth resistance tester | < 5 ohms for single electrode | Cl 8.4.9 | 5-10 min per electrode |

D3.2 Test Equipment Owned (Cost Recovery Factor)

Contractors amortise test equipment costs into inspection fees. The tool can factor this in.

| Instrument | Approximate Cost | Calibration | Useful Life | Cost per Inspection (amortised) |
| --- | --- | --- | --- | --- |
| Multifunction tester (Fluke/Megger) | R 25,000 - R 65,000 | Annual - R 3,000 - R 5,000 | 5-8 years | R 25 - R 80 |
| Insulation resistance tester | R 8,000 - R 20,000 | Annual - R 2,000 - R 3,000 | 5-10 years | R 10 - R 30 |
| Earth resistance tester | R 8,000 - R 25,000 | Annual - R 2,000 - R 4,000 | 5-8 years | R 15 - R 40 |
| RCD tester | R 5,000 - R 12,000 | Annual - R 1,500 - R 2,500 | 5-8 years | R 8 - R 20 |
| Phase rotation meter | R 2,000 - R 5,000 | None required | 10+ years | R 2 - R 5 |
| Clamp meter | R 2,000 - R 8,000 | Annual - R 1,500 | 5-8 years | R 5 - R 12 |
| Socket tester | R 300 - R 800 | None | 3-5 years | R 1 - R 3 |
| Thermal imaging camera | R 15,000 - R 45,000 | Every 2 years - R 3,000 | 5-8 years | R 20 - R 60 |

## D4. COC Document Requirements

The tool should auto-generate or include templates for these mandatory documents per the Electrical Installation Regulations (2009).

| Document | Legal Requirement | Who Signs | Content | Retention |
| --- | --- | --- | --- | --- |
| Certificate of Compliance (COC) | EIR 2009 Reg 7 | Registered person (master installer/electrician) | Declaration that installation complies with SANS 10142 | Kept by owner, copy to supplier (municipality/Eskom) |
| Test report | EIR 2009 Reg 7(2) | Registered person who conducted tests | All test results per SANS 10142 Cl 8 | Attached to COC, kept minimum 5 years |
| As-built drawings | SANS 10142 Cl 5.2 | Designer / installer | Layout showing all circuits, DB schedule, cable routes | Kept by owner, copy with COC |
| DB schedule | SANS 10142 Cl 6.5 | Installer | Circuit number, description, MCB rating, cable size, ELCB | Mounted inside DB door and on COC |
| Risk assessment (lightning) | SANS 62305-2 | Competent person | Lightning risk calculation, LPL determination | Commercial: mandatory. Residential: recommended |
| SSEG compliance report | NRS 097-2-3 | Registered person | Anti-islanding test, protection settings, grid compliance | Required for all solar installations |
| Defects list (if failed) | Best practice | Inspector | Itemised list of defects with severity and remedial scope | Provided to owner for remedial quotation |
| Photographic evidence | Best practice | Inspector | Photos of DB, earthing, defects, key installation details | Digital record, attached to report |

PART E: DATA MODEL & FORMULA ENGINE

## E1. Quotation Calculation Formulas

These are the core formulas the tool must implement for accurate pricing.

E1.1 Material Cost Calculation

material_total = SUM(item_qty x sell_price x (1 + waste_factor_pct))

sell_price = cost_price x (1 + material_markup_pct)

E1.2 Labour Cost Calculation

labour_total = SUM(point_count x rate_per_point x difficulty_multiplier)

OR (for day-rate method):

labour_total = estimated_days x (master_rate + assistant_rate) x difficulty_multiplier

estimated_days = total_points / points_per_day

points_per_day: lighting = 8-12, sockets = 6-10, dedicated circuits = 2-4

E1.3 Project Total Calculation

subtotal = material_total + labour_total

contingency = subtotal x contingency_pct

overhead = (subtotal + contingency) x overhead_pct

profit = (subtotal + contingency + overhead) x profit_margin_pct

total_excl_vat = subtotal + contingency + overhead + profit

vat = total_excl_vat x 0.15

grand_total = total_excl_vat + vat

E1.4 Solar System Specific Formulas

panels_required = CEIL(system_size_kwp x 1000 / panel_wattage)

roof_area_required_m2 = panels_required x panel_area_m2 x 1.15 (spacing factor)

annual_yield_kwh = system_size_kwp x peak_sun_hours x 365 x system_efficiency

peak_sun_hours (Pretoria) = 5.5 - 6.0 hrs/day

system_efficiency = 0.78 - 0.85 (accounts for inverter, cable, temp losses)

annual_saving = annual_yield_kwh x tariff_r_kwh

simple_payback_years = total_system_cost / annual_saving

E1.5 Cable Quantity Estimation

cable_run_length = SUM(point_distance_from_db + vertical_run + 1m_slack_each_end)

For estimation when exact layout unknown:

avg_cable_run (single storey) = (building_length + building_width) / 2 x 0.7

avg_cable_run (double storey ground) = avg_cable_run x 1.0

avg_cable_run (double storey upper) = avg_cable_run x 1.15 + floor_height

total_cable = SUM(points_per_circuit x avg_cable_run) x (1 + waste_factor)

E1.6 Maximum Demand Calculation (SANS 10142 Annex B)

max_demand = SUM(circuit_load x diversity_factor) for all circuits

| Load Type | Diversity Factor | Example |
| --- | --- | --- |
| Lighting (first 1kVA) | 1.0 | First 1kVA at 100% |
| Lighting (remainder) | 0.75 | Balance at 75% |
| Socket outlets (first 1kVA) | 1.0 | First 1kVA at 100% |
| Socket outlets (next 9kVA) | 0.5 | Next 9kVA at 50% |
| Socket outlets (remainder) | 0.25 | Balance at 25% |
| Cooking appliances (first) | 1.0 | First appliance at 100% |
| Cooking appliances (additional) | 0.5 | Each additional at 50% |
| Water heating (geyser) | 1.0 | Full load |
| HVAC (largest unit) | 1.0 | Largest unit at 100% |
| HVAC (additional units) | 0.75 | Additional units at 75% |
| Pool pump / borehole | 1.0 | Full load |
| EV charger | 1.0 | Full load (cannot be diversified) |

## E2. Database Schema Recommendations

For the full-stack version of AfriPlan, the following database tables are recommended:

| Table | Purpose | Key Fields | Relationships |
| --- | --- | --- | --- |
| projects | Master project record | id, client_id, type, subtype, location, status, created_at | Has many quotations |
| quotations | Generated quotation | id, project_id, version, total, status, valid_until | Belongs to project, has many line_items |
| line_items | Individual BOQ items | id, quotation_id, material_id, qty, unit_price, total, category | Belongs to quotation |
| materials | Product database | id, code, description, category, cost_price, sell_price, updated_at | Referenced by line_items |
| labour_rates | Labour pricing | id, task_type, rate_per_point, rate_per_day, region, updated_at | Referenced by line_items |
| rooms | Room specifications | id, project_id, room_type, area_m2, light_points, socket_points | Belongs to project |
| circuits | Circuit schedule | id, project_id, circuit_no, description, mcb_rating, cable_size, phase | Belongs to project |
| solar_systems | Solar specifications | id, project_id, system_kwp, panel_type, inverter_type, battery_kwh | Belongs to project |
| coc_inspections | COC records | id, project_id, inspector_id, date, result, defects_json | Belongs to project |
| clients | Client information | id, name, type, contact, address, payment_terms | Has many projects |
| price_history | Price tracking | id, material_id, cost_price, effective_date | Belongs to material |
| regional_factors | Location multipliers | id, region, labour_mult, material_mult, transport_cost | Referenced by projects |

## E3. Price Escalation Model

To keep the tool accurate over time, implement automatic price escalation.

| Component | Escalation Driver | Suggested Update Method | Annual Estimate (2026) |
| --- | --- | --- | --- |
| Cable (copper) | LME copper price + Rand exchange rate | Monthly API feed from commodity tracker | +8% - 12% (volatile) |
| Cable (aluminium) | LME aluminium price | Monthly API feed | +5% - 8% |
| DB boards & MCBs | PPI electrical equipment | Quarterly manual update from supplier | +6% - 8% |
| Sockets & switches | PPI + import duty | Quarterly from distributor price lists | +5% - 7% |
| LED fittings | Technology deflation + Rand | Quarterly - may decrease | +2% - 5% (or -5% for premium brands) |
| Solar panels | Global PV module index + Rand | Monthly - BNEF PV module spot price | -10% to -15% (deflationary) |
| Inverters | Technology + supply chain | Quarterly from distributor | -5% to +5% |
| Batteries (LFP) | Lithium carbonate + scale | Quarterly from distributor | -8% to -15% (deflationary) |
| Labour rates | CPI + sector demand | Annual adjustment, Jan each year | +5% - 8% |
| Transport/delivery | Fuel price index | Monthly with fuel price | +4% - 10% |
| Compliance fees (COC) | ECSA / DoL annual adjustment | Annual, April each year | +5% - 7% |

END OF SPECIFICATION DOCUMENT

AfriPlan Electrical  |  JLWanalytics  |  Version 1.0  |  February 2026

This document contains 80+ variables, 30+ tables, and complete SANS 10142 compliance mapping.